|  | Browns Ferry Nuclear Plant |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Unit 2 |  |  |  |  |  |  |  |  |  |
| Surveillance Procedure |  |  |  |  |  |  |  |  |  |
| 2-SR-3.3.1.1.9(IRM A) |  |  |  |  |  |  |  |  |  |
| Intermediate Range Monitor (IRM) Channel A Calibration |  |  |  |  |  |  |  |  |  |
| Revision 0027 |  |  |  |  |  |  |  |  |  |
| Quality Related |  |  |  |  |  |  |  |  |  |
| Level of Use: Continuous Use |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Level of Use or Other Information: Key # P2237A |  |  |  |  |  |
| Effective Date: |  |  | 03-31-2021 |  |  |  |  |  |  |
| Responsible Organization: |  |  |  |  | MIG, Instrument Maintenance |  |  |  |  |
| Prepared By: |  | Stephen Wheeler |  |  |  |  |  |  |  |
| Approved By: |  | William Maniscalco |  |  |  |  |  |  |  |

| Current Revision Description |  |  |  |
| --- | --- | --- | --- |
| Pages Affected: | 59 |  |  |
| Type of Change: | Enhancement | Tracking Number: | 029 |
| CR 1673556-001 / PCR 20000108 Step 6.12[109] Corrected 2-LPNL-925-0061 to 2-LPNL-925-0027 to match panel that pre-amp was removed from in Step 6.12[2]. |  |  |  |

Table of Contents

1.0	INTRODUCTION	5

1.1	Purpose	5

1.2	Scope	5

1.3	Frequency and Conditions	6

1.3.1	Frequency	6

1.3.2	Conditions	6

2.0	REFERENCES	7

2.1	Performance References	7

2.2	Developmental References	7

2.3	Commitments	7

3.0	PRECAUTIONS AND LIMITATIONS	8

3.1	Precautions	8

3.2	Limitations	8

4.0	PREREQUISITE ACTIONS	9

4.1	Preliminary Actions	9

4.2	Special Tools, Measuring and Test Equipment, Parts, and Supplies	11

4.2.1	Special Tools	11

4.2.2	Measuring and Test Equipment (M&TE)	12

4.3	Approvals and Notifications	14

5.0	ACCEPTANCE CRITERIA	14

6.0	PERFORMANCE	16

6.1	Initial Requirements	16

6.2	Removal From Service	18

6.3	Channel IRM A As-Found Data	18

6.4	VOLTAGE PREREGULATOR Module VR27 Calibration	23

6.5	VOLTAGE REGULATOR Module VR29 Calibration	25

6.6	MEAN SQUARE ANALOG Card (MSA) As-Found Data	27

6.7	MEAN SQUARE ANALOG (MSA) CARD Calibration	29

6.8	IRM Drawer Zero Adjust	33

6.9	INVERTER Module AR12 Calibration	34

Table of Contents (continued)

6.10	High Voltage INOP Trip Calibration	39

6.11	As-Left Trip Setpoints	41

6.12	IRM System Gain and Range Correlation	46

6.13	Functional Test of IRM Channel A with Reactor Mode Switch in RUN	61

6.14	Functional Test of IRM Channel A with Reactor Mode Switch NOT in RUN	64

7.0	POST PERFORMANCE ACTIVITY	78

7.1	Test Completion	78

8.0	RECORDS	78

Attachment 1:	Control Room Components Affected By Procedure Performance	79

Attachment 2:	TM200 To 2-RLY-92-741ATDR Test Setup	80

Attachment 3:	MSA Circuit Card Layout	81

Attachment 4:	Test Setup For IRM Channel Calibration	82

Attachment 5:	Range Switch Signal Acceptance	83

INTRODUCTION

Purpose

This procedure is performed to determine the operability of IRM function of Reactor Protection System (RPS) Instrumentation, Control Rod Block Instrumentation, and Surveillance Instrumentation in the Neutron Monitoring System (NMS).

Scope

This procedure is performed on IRM Channel A. Surveillance Requirements (SR) 2-SR-3.3.1.1.9(IRM B), 2-SR-3.3.1.1.9(IRM C), 2-SR-3.3.1.1.9(IRM D), 2-SR-3.3.1.1.9(IRM E), 2-SR-3.3.1.1.9(IRM F), 2-SR-3.3.1.1.9(IRM G), and 2-SR-3.3.1.1.9(IRM H) must also be performed to satisfy Technical Specification SR 3.3.1.1.9 and Technical Requirements Manual (TRM) Technical Surveillance Requirements (TSR) 3.3.4.6 and 3.3.5.8 for IRM Channel calibration.

When this procedure is performed with the Reactor Mode Switch NOT in RUN position this procedure also partially satisfies SR 3.3.1.1.3 and SR 3.3.1.1.4 and TSR 3.3.4.3 and TSR 3.3.4.4 relating to IRM Channel functional test and TSR 3.3.4.9 for Rod Block Logic functional test.  With the Reactor Mode Switch NOT in RUN position, 2-SR-3.3.1.1.3(IRMs) is performed to satisfy Technical Specification (TS) and TRM requirements for IRM Channel functional test.

This procedure also partially satisfies SR 3.10.3.1 and SR 3.10.4.1 relating to IRM Channel calibration and functional test.  This procedure in conjunction with those listed in Section 1.2A fully satisfies SR 3.10.3.1 and SR 3.10.4.1 relating to IRM Channel calibration and functional test.  SR 2-SR-3.3.1.1.3(IRMs) satisfies these requirements for IRM Channel functional test.

This procedure provides overlap testing for, and partially satisfies, requirements of SR 3.3.1.1.14 for RPS Instrumentation Logic System Functional Test.

INOP bypass function has been added to allow functional testing of RPS and Reactor Manual Control System (RMCS).

Frequency and Conditions

Frequency

This procedure is performed once every 92 days.

This procedure is NOT required to be performed when entering Mode 2 from Mode 1 until 12 hours after entering Mode 2.

Conditions

This procedure can be performed in any operational mode.

The following IRM functions are required to be OPERABLE in the modes listed below:

| TS/TRM Function | Mode |
| --- | --- |
| Neutron Flux - HIGH INOP | 2, 3(1), 4(1), 5(2) |
| IRM UPSCALE IRM DOWNSCALE Detector NOT in Startup Position | 2 |

| (1) | With Reactor Mode Switch in REFUEL |
| --- | --- |
| (2) | With any control rod withdrawn from a core cell containing one or more fuel assemblies |

REFERENCES

Performance References

None

Developmental References

2-SIMI-92B, Neutron Monitoring Scaling and Setpoint Document

BFN Final Safety Analysis Report (FSAR), Section 7.2, Reactor Protection System

BFN Final Safety Analysis Report (FSAR), Section 7.5, Neutron Monitoring System

BFN Final Safety Analysis Report (FSAR), Section 7.7, Reactor Manual Control

BFN Technical Requirements Manual, Section TR 3.3.4, Control Rod Block Instrumentation

BFN Technical Requirements Manual, Section TR 3.3.5, Surveillance Instrumentation Developmental References

BFN Technical Specifications, Section 3.3.1.1, Reactor Protection System (RPS) Instrumentation

BFN Technical Specifications, Section 3.10.3, Single Control Rod Withdrawal - Hot Shutdown

BFN Technical Specifications, Section 3.10.4, Single Control Rod Withdrawal - Cold Shutdown

VTD-G080-9335, SRM and IRM Preamplifier Enclosure

VTM-G080-3740, GEK-858D, Voltage preamplifier

VTM-G080-3800, GEK-27723A, Mean Square Voltage Wide Range Monitor

Commitments

PER 129518, IRM Out of Tolerance

PRECAUTIONS AND LIMITATIONS

Precautions

[PER/C]The Range 6 to 7 Correlation shall be checked any time the IRM preamp is replaced per SII-0-XX-92-054. [129518-005]

Limitations

Calibration and functional test is to be performed on one channel at a time. All trips are to be reset and channel returned to fully operable status before starting another channel, unless otherwise directed by Unit Senior Reactor Operator (Unit SRO).

Jumpers are installed if scram links have been removed, in order to test IRM logic.  These jumpers defeat non-coincidence Scram function of neutron monitoring system.  When jumpers are installed, refueling operations are to stop until completion of this procedure and removal of jumpers.

If any other IRM in RPS trip Channel A is INOP (or becomes INOP during performance of this procedure), entry into TS Conditions and Required Actions can be delayed for up to 6 hours provided associated function maintains RPS trip capability.  This procedure can exceed the 6 hour testing limit.

PREREQUISITE ACTIONS

Preliminary Actions

ENSURE STS for this procedure and work activity is included in work order. (Key # P2237A)	________

ENSURE training requirements are met prior to performance of this procedure:

IMP 563 - Conduct SI (Calibration and Functional) on Intermediate Range Neutron Monitoring System

and

IMP 556 - Conduct SI (Calibration and Functional) on Reactor Protection System	________

IF 2-HS-99-5A/S1, REACTOR MODE SWITCH, is NOT in RUN, THEN

PERFORM the following, otherwise, MARK steps N/A:

CHECK RPS Sub Channel Trip does NOT exist.	________

CHECK no other test or maintenance is in progress that is going to provide a half scram signal to RPS logic.	________

IF prerequisites in Steps 4.1[3.1] OR 4.1[3.2] are NOT met, THEN

OBTAIN Unit SRO permission to continue.  Otherwise, MARK N/A.

| Unit SRO Signature |  | Date |
| --- | --- | --- |

IF 2-HS-99-5A/S1, REACTOR MODE SWITCH, is NOT in RUN, THEN

PERFORM the following, otherwise, MARK steps N/A:

CHECK Control Rod Drive (CRD) platform is in NORMAL position.	________

IF IRM cables are NOT routed in normal configuration, THEN

MONITOR movement of IRM cables by direct observation or remote video camera.  Otherwise, MARK N/A.	________

Special Tools, Measuring and Test Equipment, Parts, and Supplies

Special Tools

OBTAIN the following:

Plug-in adapter GE129B2048G1 and G2

Test Cable G.E. 175A9111G01

Hewlett Packard Oscillator, Model 651B or 652A

Two Oscilloscope probes (matched pair) labeled Inverter Test Cable

2000 pF Capacitor (Substitution box is NOT acceptable)

HV-1 Test Box

J4 Adapter

Three BNC to UHF Adapters

BNC-T connector

BNC - Barrel

Six Coax Cables

J-42 Test Cable

MEAN SQUARE ANALOG Module Test Cover

Calculator

Isolation transformer

Two pronged adapter	________

IF Reactor Mode Switch is NOT in RUN, THEN

OBTAIN Two Volt Ohm Meters (VOMs).  Otherwise, MARK N/A.	________

IF RPS shorting links are removed AND Reactor Mode Switch is NOT in RUN, THEN

OBTAIN two 12-14 inch jumpers with discs.  Otherwise, MARK N/A.	________

Measuring and Test Equipment (M&TE)

NOTES

If it is necessary to change M&TE, then identification number, calibration due date and step numbers for new M&TE used is documented in remarks section of STS. M&TE Used (Y or N) column will be completed in performance of Step 7.1[3]. Only two Digital Multimeters (DMM) are required.

OBTAIN M&TE listed in M&TE table.	________

RECORD M&TE data in M&TE table.	________

| M&TE Table |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Parameter | Recommended Instrument |  | Required Range | Required Accuracy |  |
| Voltage | Digital Multimeter |  | 0-100 Vdc | 1.0 Vdc | M&TE Used |
|  | TVA ID# | Cal. Due Date | Actual Range | Actual Accuracy | (Y or N) |
| Voltage | Digital Multimeter |  | 0-1 Vdc | 0.004 Vdc | M&TE Used |
|  | TVA ID# | Cal. Due Date | Actual Range | Actual Accuracy | (Y or N) |
| Voltage | Digital Multimeter |  | 0-4.20 Vdc | 0.005 Vdc | M&TE Used |
|  | TVA ID# | Cal. Due Date | Actual Range | Actual Accuracy | (Y or N) |
| Torque | Torque Wrench |  | 20 In-lbs | N/A | M&TE Used |
|  | TVA ID# | Cal. Due Date | Actual Range | Actual Accuracy | (Y or N) |
|  |  |  |  | N/A |  |
| Volts RMS | RMS Voltmeter |  | N/A | N/A | M&TE Used |
|  | TVA ID# | Cal. Due Date | Actual Range | Actual Accuracy | (Y or N) |
|  |  |  | N/A | N/A |  |
| Wave form | Oscilloscope (Dual Trace) |  | N/A | N/A | M&TE Used |
|  | TVA ID# | Cal. Due Date | Actual Range | Actual Accuracy | (Y or N) |
|  |  |  | N/A | N/A |  |
| Test Fixture | IRM Test Fixture G.E. 117C2956G001 |  | N/A | N/A | M&TE Used |
|  | TVA ID# | Cal. Due Date | Actual Range | Actual Accuracy | (Y or N) |
|  |  |  | N/A | N/A |  |
| Time | Programma TM200 Timer |  | N/A | N/A | M&TE Used |
|  | TVA ID# | Cal. Due Date | Actual Range | Actual Accuracy | (Y or N) |
|  |  |  | N/A | N/A |  |

ENSURE, with Peer Check, applicable M&TE meets or exceeds Required Range.	________

ENSURE, with Peer Check, applicable M&TE is equal to or better than Required Accuracy.	________

Approvals and Notifications

EVALUATE operability of Intermediate Range Monitoring System based on current operability status of IRM’s C, E, and G.

| Unit SRO Signature |  | Date |  |  |
| --- | --- | --- | --- | --- |

OBTAIN Unit SRO authorization to begin.	________

ACCEPTANCE CRITERIA

Responses which fail to meet Acceptance Criteria (AC) constitute unsatisfactory surveillance procedure results and require immediate notification of Unit SRO.

The following AC are applicable in all mode switch positions:

When high voltage power supply is lowered to 90 Vdc (88 to 92 Vdc) the INOP indicating light on CHANNEL A IRM drawer ILLUMINATES. (TS/TRM)

As-found DOWNSCALE, UPSCALE HIGH, and UPSCALE HIGH HIGH trip setpoints are within TS/TRM Allowable Values.

DOWNSCALE - Greater than or equal to 0.040

UPSCALE HIGH - Less than or equal to 0.864

UPSCALE HIGH HIGH - Less than or equal to 0.960

When an internal signal is applied to IRM front panel meter, the front panel meter responds with an indication of between 38 and 42 UNITS on the 125 UNITS scale. (TRM)

The following AC are only applicable when 2-HS-99-5A/S1, REACTOR MODE SWITCH is NOT in RUN.

When simulated DOWNSCALE condition is sensed by IRM, annunciator CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7) alarms or contacts OPEN in rod block logic circuit. (TRM)

When simulated UPSCALE HIGH condition is sensed by IRM, annunciator CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7) comes in ALARM or contacts open in rod block logic circuit.(TRM)

When simulated UPSCALE HIGH HIGH condition is sensed by IRM, SCRAM SOLENOID GROUP A LOGIC RESET indicating lights EXTINGUISH. (TS)

When IRM Mode switch is in a position other than OPERATE, an INOP condition is sensed by IRM and the following occurs:

SCRAM SOLENOID GROUP A LOGIC RESET indicating lights EXTINGUISH. (TS)

CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7) alarms or contacts OPEN in rod block logic circuit. (TRM)

When IRM A detector is withdrawn until IN indicating light is EXTINGUISHED, CONTROL ROD WITHDRAWAL BLOCK 
(2-XA-55-5A, window 7) alarms or contacts OPEN in rod block logic circuit. (TRM)

NOTE

Completion of steps performed by an operator or another Instrument Mechanic (IM) can be identified by placing that persons initials in the blank first followed by word “by” or a slash (/), then initials of the IM recording completion. Examples: OP or IM by IM OP or IM/IM

PERFORMANCE

Initial Requirements

NOTIFY UO procedure is commencing.	________

CHECK following annunciators are CLEAR:

NEUTRON MONITORING SYS HALF SCRAM (2-XA-55-4A, window 16)	________

REACTOR CHANNEL A AUTO SCRAM (2-XA-55-5B, window 1)	________

REACTOR CHANNEL B AUTO SCRAM (2-XA-55-5B, window 2)	________

IRM HIGH (2-XA-55-5A, window 26)	________

IRM CHAN A, C, E, G HI-HI/INOP (2-XA-55-5A, window 33)	________

IRM CHAN B, D, F, H HI-HI/INOP (2-XA-55-5A, window 34)	________

IF none of the other IRMs are DOWNSCALE, THEN

CHECK IRM DOWNSCALE (2-XA-55-5A, window 19) is CLEAR.  Otherwise, MARK N/A.	________

CHECK following indicating lights are ILLUMINATED on Panel 2-9-5:

SCRAM SOLENOID GROUP A LOGIC RESET indicating lights (4)	________

SCRAM SOLENOID GROUP B LOGIC RESET indicating lights (4)	________

2-IL-99-5A/AB, SYSTEM A BACKUP SCRAM VALVE 
indicating lights (2)	________

2-IL-99-5A/CD, SYSTEM B BACKUP SCRAM VALVE 
 indicating lights (2)	________

PROVIDE UO a copy of Attachment 1, Control Room Components Affected By Procedure Performance.	________

REQUEST UO or designee annotate the following at Recorder 2-XR-92-7/46A Channel 3 on Panel 2-9-5:

Channel 3

2-SR-3.3.1.1.9(IRM A)

Initials	________

NOTE

Local trips may be reset as needed throughout the procedure.

Removal From Service

REQUEST UO place IRM A in BYPASS by placing 2-HS-92-7A/S4A, IRM BYPASS, in CH-A Position.	________

IF 2-HS-99-5A/S1, REACTOR MODE SWITCH is NOT in RUN, THEN

CHECK CHAN A IRM BYPASSED indicating light is ILLUMINATED on Panel 2-9-5.  Otherwise, MARK N/A.	________

CHECK BYPASSED IRM CH A indicating light is ILLUMINATED on Panel 2-9-12.	________

OPEN CHANNEL A IRM drawer on Panel 2-9-12.	________

IF no other IRMs are bypassed AND computer is OPERABLE, AND 2-HS-99-5A/S1, REACTOR MODE SWITCH is NOT in RUN THEN

CHECK computer point DIG125 indicates BYPASS.  Otherwise, MARK N/A.	________

RECORD date and time channel removed from service.

| Date |  | Time |  |  | ________ |
| --- | --- | --- | --- | --- | --- |

NOTE

All actions will be performed at CHANNEL A IRM drawer unless otherwise stated.

Channel IRM A As-Found Data

DISCONNECT preamp input cable from J1 in IRM drawer.	________

ADJUST amplitude controls on test oscillator for minimum voltage output.	________

ADJUST oscillator output frequency to 100 KHz.	________

Using BNC-T connector, CONNECT RMS voltmeter to test oscillator 600 output cable.	________

CONNECT test oscillator to J1.	________

REQUEST UO place 2-XS-92-7/42A, CHANNEL A IRM RANGE SWITCH in Position 2.	________

RAISE oscillator amplitude until IRM front panel meter indicates 15 UNITS on black scale.	________

RESET local IRM alarms using RESET switch on IRM drawer.	________

CHECK following local indicating lights on IRM drawer are EXTINGUISHED:

DOWNSCALE	________

UPSCALE HIGH	________

UPSCALE HIGH HIGH.	________

INOP	________

DISCONNECT recorder cable from J4 in IRM drawer.	________

CONNECT J4 adapter to J4 at rear of IRM drawer.	________

PLACE DMM on 2 Vdc scale.	________

CONNECT DMM to J4 adapter test jacks H(+) and K(-).	________

APPLY power to Programma TM200 timer.	________

SET START and STOP functions as shown in Attachment 2, TM200 To 2-RLY-92-741ATDR Test Setup.	________

On top of 2-RLY-92-741ATDR, CONNECT TM200 START terminals to coil terminals 12VDC(+) and 12VDC(-).	________

On top of 2-RLY-92-741ATDR, CONNECT TM200 STOP terminals to contact terminals Common and Normally Open.	________

LOWER oscillator amplitude until IRM DOWNSCALE light is ILLUMINATED.	________

RECORD As-found DMM indication for IRM DOWNSCALE trip point in Table 1.	________

RAISE oscillator amplitude until IRM UPSCALE HIGH light is ILLUMINATED.	________

RECORD As-found DMM indication for IRM UPSCALE HIGH trip point in Table 1.	________

PRESS RESET on TM200 to ensure timer is ready to capture trigger events.	________

RAISE oscillator amplitude until IRM UPSCALE HIGH HIGH light is ILLUMINATED.	________

RECORD As-found DMM indication for UPSCALE HIGH HIGH trip point in Table 1.	________

RECORD As-found TM200 value in Table 2	________

| Table 1 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Trip Function | Desired Vdc | Min Vdc | As-found Vdc | As-left Vdc | Max Vdc | TS/TRM Allowable Value Vdc |
| DOWNSCALE | 0.060 | 0.048 |  |  | 0.072 | 0.040 |
| UPSCALE HIGH | 0.720 | 0.700 |  |  | 0.740 | 0.864 |
| UPSCALE HIGH HIGH | 0.931 | 0.911 |  |  | 0.951 | 0.960 |

| Table 2 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Time Delay Relay |  |  |  |  |  |
| Desired | Min | As-found | As-left | Max | Max Allowable |
| 700 ms | 630 ms |  |  | 770 ms | 800 ms |

CHECK As-found trip setpoints are within TS/TRM Allowable values listed in Table 1.	_____(AC)

IF As-found value in Table 2 is within Min/Max values, THEN

PERFORM the following, otherwise MARK steps N/A:

RECORD As-found value in As-left column of Table 2.	________

MARK Step 6.3[28] through 6.3[29.9] N/A.	________

IF As-found value in Table 2 is greater than 800 ms, THEN

INITIATE CR to document and correct component failure, otherwise, MARK N/A.	________

IF As-found value in Table 2 is outside Min/Max values, THEN

PERFORM the following.  Otherwise, MARK steps N/A:

REMOVE cover from DELAY ADJ. potentiometer on 2-RLY-92-741ATDR.	________

LOWER oscillator amplitude until IRM UPSCALE HIGH HIGH light is EXTINGUISHED.

PRESS RESET on TM200 to ensure timer is ready to capture trigger events.

ADJUST DELAY ADJ. potentiometer on 2-RLY-92-741ATDR to either raise (CW) or lower (CCW) time delay.

RAISE oscillator amplitude until IRM UPSCALE HIGH HIGH light is ILLUMINATED.

COMPARE new TDR value to Min/Max values in Table 2.

IF values are outside Min/Max values in Table 2, THEN

REPEAT Steps 6.3[29.2] through 6.3[29.6], otherwise MARK N/A.	________

REPLACE cover on DELAY ADJ. potentiometer.	________

RECORD As-left value in As-left column of Table 2.	________

DISCONNECT TM200 from top of 2-RLY-92-741ATDR.	________

REMOVE power from Programma TM200 timer.	________

RAISE oscillator output amplitude until DMM indication is 1.000 Vdc (0.990 Vdc to 1.010 Vdc).	________

RECORD RMS voltmeter indication.

| ______________ mVac. |  | ________ |
| --- | --- | --- |

IF RMS voltmeter reading in Step 6.3[33] is NOT 30 to 60 mVac THEN

NOTIFY Foreman or Cognizant Engineer prior to continuing.  Otherwise, MARK N/A.	________

CONNECT IRM Test Fixture to 120 Vac power source.	________

TURN S4 to ON to allow for 10 minute warm-up before Section 6.6 is begun.

| Time |  |  | ________ |
| --- | --- | --- | --- |

VOLTAGE PREREGULATOR Module VR27 Calibration

REMOVE VOLTAGE PREREGULATOR Module VR27 from IRM drawer.	________

INSTALL plug-in adapter GE129B2048G 001 in place of VOLTAGE PREREGULATOR Module VR27.	________

INSTALL VOLTAGE PREREGULATOR Module VR27 on plug-in adapter.	________

CONNECT DMM on 200 Vdc scale between TP 17(+) and TP 3 (common) on plug-in adapter.	________

RECORD As-found value in As-found (+)20 Vdc column of Table 3.	________

| Table 3 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Power Supply | Desired Vdc | Min Vdc | As-found Vdc | As-left Vdc | Max Vdc |
| (+)20 Vdc | 20.00 | 19.90 |  |  | 20.10 |
| (-)20 Vdc | (-)20.00 | (-)19.90 |  |  | (-)20.10 |

IF As-found output voltage of (+)20 Volt VOLTAGE PREREGULATOR Module VR27 is NOT within 19.90 to 20.10 Vdc, THEN

PERFORM the following, otherwise, MARK steps N/A:

IF R9 is NOT accessible, THEN

REMOVE cover from VOLTAGE PREREGULATOR Module VR27.  Otherwise, MARK N/A.	________

ADJUST R9 on VOLTAGE PREREGULATOR Module VR27 to obtain indication of (+)20.00 Vdc (19.90 to 20.10 Vdc) on DMM.	________

RECORD value in As-left (+)20 Vdc column of Table 3.	________

MOVE DMM lead from TP 17(+) to TP 1 (-).	________

RECORD As-found (-)20 Vdc voltage in As-found (-)20 Vdc column of Table 3.	________

IF As-found output voltage of (-20) Volt VOLTAGE PREREGULATOR Module VR27 is NOT within (-)19.90 to (-) 20.10 Vdc, THEN

PERFORM the following, otherwise, MARK steps N/A:

IF R20 is NOT accessible, THEN

REMOVE cover from VOLTAGE PREREGULATOR Module VR27.  Otherwise, MARK N/A.	________

ADJUST R20 on VOLTAGE PREREGULATOR Module VR27 to obtain indication of (-)20.00 Vdc
 ((-)19.90 to (-)20.10 Vdc) on DMM.	________

RECORD value in As-left (-)20 Vdc column of Table 3.	________

DISCONNECT DMM.	________

REMOVE plug-in adapter.	________

REMOVE VOLTAGE PREREGULATOR Module VR27 from plug-in adapter.	________

IF cover on VOLTAGE PREREGULATOR Module VR27 was removed, THEN

REPLACE cover on VOLTAGE PREREGULATOR Module VR27.  Otherwise, MARK N/A.	________

REINSTALL VOLTAGE PREREGULATOR Module VR27 in IRM drawer.	________

VOLTAGE REGULATOR Module VR29 Calibration

CONNECT DMM on 20 Vdc scale between J1(+) and J2 (common) on VOLTAGE REGULATOR Module VR29.	________

RECORD As-found (+)15 Vdc voltage in Table 4.	________

MOVE positive lead of DMM from J1 to J3 on VOLTAGE REGULATOR Module VR29.	________

RECORD As-found (-)15 Vdc voltage in Table 4.	________

| Table 4 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Power Supply | Desired Vdc | Min Vdc | As-found Vdc | As-left Vdc | Max Vdc |
| (+)15 Vdc | (+)15.00 | (+)14.90 |  |  | (+)15.10Vdc |
| (-)15 Vdc | (-)15.00 | (-)14.90 |  |  | (-)15.10Vdc |

DISCONNECT DMM.	________

IF As-found voltages of VOLTAGE REGULATOR Module VR29 are within tolerance, THEN

PERFORM the following, otherwise, MARK steps N/A:

RECORD As-found values in the As-left columns of Table 4.	________

MARK Steps 6.5[7] through 6.5[20] N/A.	________

REMOVE VOLTAGE REGULATOR Module VR29.	________

IF R9 and R12 are NOT accessible, THEN

REMOVE VOLTAGE REGULATOR Module VR29 cover.  Otherwise, MARK N/A.	________

PLACE VOLTAGE REGULATOR Module VR29 on GE129B2048G1 plug-in adapter.	________

INSTALL VOLTAGE REGULATOR Module VR29 with GE129B2048G1 plug-in adaptor in IRM drawer.	________

CONNECT DMM between J1(+) and J2(-) on VOLTAGE REGULATOR Module VR29.	________

ADJUST R9 to obtain an indication of (+)15.00 Vdc (14.90 to 15.10 Vdc) on DMM.	________

MOVE positive lead of DMM from J1 to J3 on VOLTAGE REGULATOR Module VR29.	________

ADJUST R12 to obtain an indication of (-)15.00 Vdc ((-)14.90 to (-)15.10 Vdc) on DMM.	________

REPEAT Steps 6.5[11] through 6.5[14] until both (+)15 Vdc and (-)15 Vdc indications are within tolerance and no further adjustment is required.  Otherwise, MARK N/A.	________

RECORD As-left voltages in Table 4.	________

DISCONNECT DMM.	________

REMOVE VOLTAGE REGULATOR Module VR29 and GE129B2048G1 plug-in adapter from IRM drawer.	________

IF VOLTAGE REGULATOR Module VR29 cover was removed, THEN

REPLACE cover.  Otherwise, MARK N/A.	________

REINSTALL VOLTAGE REGULATOR Module VR29 in IRM drawer.	________

MEAN SQUARE ANALOG Card (MSA) As-Found Data

CONNECT test lead between J8 (-)15 jack on IRM TEST FIXTURE and J3 (-) on VR29 in IRM drawer.	________

CONNECT test lead between COM (J7) jack on IRM TEST FIXTURE and J2 (common) on VR29 in IRM drawer.	________

CONNECT test lead between J6 (+)15 jack on IRM TEST FIXTURE and J1(+) on VR29 in IRM drawer.	________

REMOVE MEAN SQUARE ANALOG CARD Z13 from IRM drawer.	________

INSTALL MEAN SQUARE ANALOG CARD Z13 to J5 on IRM TEST FIXTURE.	________

COVER MEAN SQUARE ANALOG CARD Z13 with module test cover to protect it from drafts.	________

ENSURE 10 minute warm-up time has occurred since IRM TEST FIXTURE was turned ON in Step 6.3[36].

| Time |  |  | ________ |
| --- | --- | --- | --- |

CONNECT DMM to Output jacks (+)J9 and (-)J10 on IRM TEST FIXTURE.	________

NOTE

Waiting 1 to 3 minutes after each switch position change allows voltage readings to stabilize prior to taking reading.

PLACE INPUT SELECTOR switch (S2) and VOLTAGE switch (S3) to positions listed in Table 5.	________

RECORD voltage values from DMM in As-found Vdc column of Table 5.	________

| Table 5 |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| INPUT SELECTOR (S2) | VOLTAGE SELECTOR (S3) | Desired Vdc | Min Vdc | LAI MIN Vdc | As-found Vdc | As-left Vdc | LAI MAX Vdc | Max Vdc |
| 1 | 1 | 10.00 | 9.80 | 9.90 |  |  | 10.10 | 10.20 |
| 3 | 1 | 10.00 | 9.80 | 9.90 |  |  | 10.10 | 10.20 |
| 3 | 2 | 6.40 | 6.20 | 6.30 |  |  | 6.50 | 6.60 |
| 1 | 2 | 6.40 | 6.20 | 6.30 |  |  | 6.50 | 6.60 |
| 1 | 3 | 3.60 | 3.40 | 3.50 |  |  | 3.70 | 3.80 |
| 3 | 3 | 3.60 | 3.40 | 3.50 |  |  | 3.70 | 3.80 |
| 3 | 4 | 1.60 | 1.50 | 1.55 |  |  | 1.65 | 1.70 |
| 1 | 4 | 1.60 | 1.50 | 1.55 |  |  | 1.65 | 1.70 |
| 1 | 5 | 0.40 | 0.30 | 0.35 |  |  | 0.45 | 0.50 |
| 3 | 5 | 0.40 | 0.30 | 0.35 |  |  | 0.45 | 0.50 |
| 3 | 6 | 0.10 | 0.00 | 0.05 |  |  | 0.15 | 0.20 |
| 1 | 6 | 0.10 | 0.00 | 0.05 |  |  | 0.15 | 0.20 |

CHECK all As-found voltages in Table 5 are within MIN/MAX values.	________

IF all As-found voltages in Table 5 are within LAI Min/ LAI Max values, THEN 

PERFORM the following, otherwise, MARK steps N/A:

RECORD As-found values in As-left Vdc column of Table 5.	________

DISCONNECT DMM.	________

DISCONNECT all test equipment from IRM drawer and IRM TEST FIXTURE.	________

REMOVE MEAN SQUARE ANALOG CARD Z13 from IRM TEST FIXTURE.	________

REINSTALL MEAN SQUARE ANALOG card Z13 in IRM drawer.	________

MARK Section 6.7 N/A.	________

MEAN SQUARE ANALOG (MSA) CARD Calibration

IF access to junction VR1/VR2(-) AND Junction R10/R13(+) OR TP1 is NOT available with cover installed, THEN

REMOVE metal back cover from MEAN SQUARE ANALOG unit.  Otherwise, MARK N/A.	________

CONNECT DMM between the junction VR1/VR2(-) [left side of VR1] and the junction R10/R13(+) or TP1, card. (Reference Attachment 3, MSA Circuit Card Layout.)	________

COVER MEAN SQUARE ANALOG CARD Z13 with module test cover to protect it from drafts.	________

PLACE IRM TEST FIXTURE Input Selector switch (S2) in Position 2.	________

PLACE Voltage Switch (S3) in Position 6.	________

RECORD As-found DMM voltage in Table 6.	________

| Table 6 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Desired Vdc | Min Vdc | As-found Vdc | As-left Vdc | Max Vdc |
| 4.200 | 4.195 |  |  | 4.205 |

IF As-found voltage in Table 6 is within Min/Max values, THEN

PERFORM the following, otherwise, MARK steps N/A:

RECORD As-found value in the As-left Vdc column of Table 6.	________

DISCONNECT DMM.	________

MARK Steps 6.7[8] through 6.7[13] N/A.	________

ADJUST R10 for DMM reading of 4.200 Vdc  (4.195 to 4.205 Vdc).	________

RECORD As-left DMM voltage in Table 6.	________

DISCONNECT DMM.	________

CONNECT DMM to output jacks (+)(J9) and (-)(J10) on IRM TEST FIXTURE.	________

NOTE

Waiting 1 to 3 minutes after each switch position change allows voltage readings to stabilize prior to taking reading.

Using the switch positions listed in Table 5, PLACE INPUT SELECTOR Switch (S2) and VOLTAGE Switch (S3) to positions listed.	________

CHECK voltages taken in Step 6.7[12].	________

IF all voltages in Step 6.7[12] are within LAI Min/ LAI Max values, THEN

PERFORM the following, otherwise, MARK steps N/A:

RECORD values in As-left column of Table 5.	________

MARK Steps 6.7[14] through 6.7[37] N/A.	________

ENSURE DMM is connected to Output jacks (+)(J9) and (-)(J10) on IRM TEST FIXTURE.	________

ENSURE Input Selector Switch (S2) is in Position 2.	________

ENSURE Voltage Switch (S3) is on Position 6.	________

ADJUST R11 fully clockwise.	________

ADJUST R9 for a DMM reading of 0.035 Vdc (0.030 to 0.040 Vdc).	________

PLACE Input Selector Switch (S2) in Position 3.	________

PLACE Voltage Switch (S3) in Position 6.	________

ADJUST R11 for a DMM reading of 0.10 Vdc (0.05 to 0.15 Vdc).	________

PLACE Voltage Switch (S3) in Position 5.	________

ADJUST R17 for a DMM reading of 0.40 Vdc (0.35 to 0.45 Vdc).	________

PLACE Voltage Switch (S3) in Position 4.	________

ADJUST R16 for a DMM reading of 1.60 Vdc (1.55 to 1.65 Vdc).	________

PLACE Voltage Switch (S3) in Position 3.	________

ADJUST R15 for a DMM reading of 3.60 Vdc (3.50 to 3.70 Vdc).	________

PLACE Voltage Switch (S3) in Position 2.	________

ADJUST R14 for a DMM reading of 6.40 Vdc (6.30 to 6.50 Vdc).	________

PLACE Voltage Switch (S3) in Position 1.	________

ADJUST R13 for a DMM reading of 10.00 Vdc (9.90 to 10.10 Vdc).	________

PLACE Input Selector Switch (S2) in Position 1.	________

PLACE Voltage switch (S3) in Position 4.	________

ADJUST R5 for a DMM reading of 1.60 Vdc (1.55 to 1.65 Vdc).	________

NOTE

Waiting 1 to 3 minutes after each switch position change allows voltage readings to stabilize prior to taking reading.

PLACE INPUT SELECTOR Switch (S2) and VOLTAGE Switch (S3) to positions listed in Table 5.	________

CHECK voltages taken in Step 6.7[35].	________

IF all voltages are NOT within tolerance, THEN

REPEAT Steps 6.7[19] through 6.7[35], until all voltage readings are within tolerance.  Otherwise, MARK N/A.	________

WHEN all voltages are within tolerance, THEN

RECORD values in the As-left column of Table 5.	________

DISCONNECT all test equipment from IRM drawer and IRM TEST FIXTURE.	________

REMOVE MEAN SQUARE ANALOG CARD Z13 from IRM TEST FIXTURE.	________

IF metal back was removed, THEN

REPLACE metal back.  Otherwise, MARK N/A.	________

INSTALL MEAN SQUARE ANALOG CARD Z13 in IRM drawer.	________

IRM Drawer Zero Adjust

CONNECT DMM, on 2 Vdc range, between J1(+) on DC AMPLIFIER AR15 and J2 (common) on VOLTAGE REGULATOR Module VR29.	________

PLACE IRM Mode switch to ZERO 1 position.	________

RECORD As-found ZERO 1 voltage in Table 7.	________

PLACE IRM Mode switch to ZERO 2 position.	________

RECORD As-found ZERO 2 voltage in Table 7.	________

| Table 7 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Switch Position | Desired Vdc | Min Vdc | As-found Vdc | As-left Vdc | Max Vdc |
| ZERO 1 | 0.000 | (-)0.005 |  |  | 0.005 |
| ZERO 2 | 0.000 | (-)0.005 |  |  | 0.005 |

IF both ZERO 1 and ZERO 2 As-found voltages are within tolerance, THEN

PERFORM the following, otherwise, MARK steps N/A:

RECORD As-found values in As-left column of Table 7.	________

MARK Steps 6.8[7] through 6.8[12] N/A.	________

PLACE IRM Mode switch to ZERO 2 position.	________

ADJUST R11 (ZERO 2 adjustment) on FEEDBACK UNIT Z14 to obtain an indication of 0.000 Vdc. ((-)0.005 Vdc to (+)0.005 Vdc)	________

PLACE IRM Mode switch to ZERO 1 position.	________

ADJUST R1 (for Type G3 card) or R2 (for Type G1 card) on DC AMPLIFIER AR15 to obtain an indication of 0.000 Vdc. ((-)0.005 Vdc to (+)0.005 Vdc)	________

IF both voltages are NOT within tolerance, THEN

REPEAT Steps 6.8[7] through 6.8[10] until interaction is minimized and both voltages are within tolerance.  Otherwise, MARK N/A.	________

RECORD final values in the As-left column of Table 7.	________

IF 0 UNITS are NOT indicated on black scale, THEN

ADJUST mechanical ZERO on front panel to obtain 0 UNITS indication on the black scale.  Otherwise, MARK N/A.	________

REMOVE DMM from VOLTAGE REGULATOR Module VR29 and DC AMPLIFIER AR15.	________

INVERTER Module AR12 Calibration

REMOVE CALIBRATION & DIODE LOGIC UNIT Z10 from IRM drawer.	________

REMOVE AMPLIFIER & ATTENUATOR Module AR11 from IRM drawer.	________

PLACE IRM Mode switch to STANDBY position.	________

CONNECT DMM between J1(+) on FEEDBACK UNIT Z14 and J2(-) common on VOLTAGE REGULATOR VR29.	________

RECORD DMM indication in space below.

| ______________Vdc. |  | ________ |
| --- | --- | --- |

IF using INVERTER TEST CABLE, THEN

PERFORM the following, otherwise, MARK steps N/A:

CONNECT INVERTER TEST CABLE to oscilloscope.	________

INSERT INVERTER TEST CABLE into INVERTER Module AR12 Test Points J1 and J2.	________

CONNECT INVERTER TEST CABLE ground to chassis ground.	________

MARK Steps 6.9[7] through 6.9[9] N/A.	________

PERFORM compensation adjustment on oscilloscope probes and amplifiers to ensure they are matched.	________

CONNECT two oscilloscope probes to INVERTER Module AR12 Test Points J1 and J2.	________

CONNECT each probe ground to chassis ground.	________

Using BNC-T connector, CONNECT RMS voltmeter to test oscillator output cable.	________

NOTE

J11-A3 is receptacle into which AMPLIFIER & ATTENUATOR Module AR11 plugs.

Using test Cable GE 175A9111G01, CONNECT output signal from test oscillator  to J11-A3 in IRM drawer in place of AMPLIFIER & ATTENUATOR Module AR11.	________

ADJUST test oscillator frequency for 500 KHz and amplitude for a 0.5V RMS output.	________

IF two equal amplitude, 180 out of phase signals are displayed on the oscilloscope display, THEN

CONTINUE.  Otherwise, MARK Steps 6.9[14] through 6.9[15.2] N/A.	________

RAISE output frequency of test oscillator to 5 MHz.	________

IF two equal amplitude, 180 out of phase signals are displayed on the oscilloscope display, THEN

PERFORM the following, otherwise, MARK steps N/A.	________

REMOVE two oscilloscope probes.	________

MARK Steps 6.9[16] through 6.9[29] N/A.	________

REMOVE INVERTER MODULE AR12 from IRM drawer.	________

IF R7 AND C2 on INVERTER Module AR12 are NOT accessible, THEN

REMOVE cover from INVERTER Module AR12.  Otherwise, MARK N/A.	________

INSTALL INVERTER Module AR12 on GE129B2048G2 plug-in adapter.	________

INSTALL INVERTER Module AR12 and GE129B2048G2 plug-in adapter in INVERTER Module AR12 location in IRM drawer.	________

ADJUST test oscillator frequency for 500 KHz and amplitude for a 0.5 volt RMS output.	________

IF two equal amplitude, 180 out of phase signals are NOT displayed on oscilloscope, THEN

ADJUST R7 until two equal amplitude, 180 out of phase signals are displayed on oscilloscope.  Otherwise, MARK N/A.	________

RAISE output frequency of test oscillator to 5 MHz.	________

IF two equal amplitude, 180 out of phase signals are NOT displayed on oscilloscope, THEN

PERFORM the following, otherwise, MARK steps N/A:

ADJUST C2 until two equal amplitude, 180 out of phase signals are displayed on oscilloscope.	________

REPEAT Steps 6.9[20] through 6.9[23.1] until interaction between two adjustments is minimized.	________

IF inverter cable was connected, THEN

 REMOVE inverter cable.  Otherwise, MARK N/A.	________

IF oscilloscope probes were connected, THEN

REMOVE oscilloscope probes. Otherwise, MARK N/A	________

REMOVE plug-in adapter and INVERTER Module AR12 from IRM drawer.	________

REMOVE INVERTER Module AR12 from GE129B2048G2 plug-in adapter.	________

IF cover was removed, THEN

REPLACE cover on INVERTER Module AR12.  Otherwise, MARK N/A.	________

REINSTALL INVERTER Module AR12, without plug-in adapter, in IRM drawer in INVERTER Module AR12 location.	________

REINSTALL CALIBRATION & DIODE LOGIC Module Z10.	________

LOWER output frequency of test oscillator to 100 KHz.	________

RECORD DMM indication from Step 6.9[5] in Step 6.9[33].	________

SUBTRACT 10 Vdc from that value.

|  |  | Vdc from Step 6.9[5] |  |
| --- | --- | --- | --- |
| - | 10 Vdc |  |  |
| = |  | Vdc | ________ |

________
	IV

RAISE output signal amplitude of test oscillator to obtain DMM reading equal to value calculated in Step 6.9[33].	________

ENSURE RMS voltmeter is connected to measure output level of test oscillator and test cable from J11-A3.	________

RECORD output value of RMS voltmeter in Table 8.	________

| Table 8 |  |  |  |
| --- | --- | --- | --- |
| Desired Vac | Min Vac | As-found Vac | Max Vac |
| 1.58 | 1.43 |  | 1.73 |

IF As-found value in Table 8 is outside Min/Max, THEN 

PERFORM the following, otherwise, MARK steps N/A:

NOTIFY Unit SRO.	________

INITIATE Condition Report (CR).	________

CORRECT problem prior to continuing.	________

DISCONNECT the following test equipment:

Test oscillator	________

RMS voltmeter	________

Test cable from J11-A3	________

REINSTALL AMPLIFIER & ATTENUATOR Module AR11 in IRM drawer.	________

DISCONNECT DMM connected between J1(+) on FEEDBACK UNIT Z14 and J2(-) common on Regulator VR29.	________

CONNECT preamp cable to J1 in IRM drawer.	________

PLACE IRM Mode switch to OPERATE.	________

High Voltage INOP Trip Calibration

DISCONNECT high voltage cable from J7 in IRM drawer.	________

CONNECT DMM to monitoring terminals red(+) and black(-) on Special High Voltage Test Box.	________

CONNECT Special High Voltage Test Box, to J7.	________

CONNECT high voltage cable (cable disconnected from J7) to test box.	________

RECORD As-found high voltage as read on DMM in Table 9.	________

| Table 9 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Desired Vdc | Min Vdc | As-found Vdc | As-left Vdc | Max Vdc |
| 100.0 | 99.0 |  |  | 101.0 |

Using R1 on POWER SUPPLY CARD in slot PS 24, ADJUST high voltage until INOP indicating light on IRM drawer just ILLUMINATES.	________

CHECK INOP indicating light on IRM drawer is ILLUMINATED.	_____(AC)

RECORD As-found high voltage trip point as read on DMM in Table 10.	________

| Table 10 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Desired Vdc | Min Vdc | As-found Vdc | As-left Vdc | Max Vdc |
| 90.0 | 88.0 |  |  | 92.0 |

CHECK As-found high voltage trip point voltage is 90.0 Vdc (88.0 to 92.0 Vdc).	_____(AC)

IF As-found INOP trip voltage is 90.0 Vdc (88.0 to 92.0 Vdc), THEN

PERFORM the following, otherwise, MARK steps N/A:

RECORD As-found voltage in As-left column of Table 10.	________

MARK Steps 6.10[11] through 6.10[17] N/A.	________

Using R1 on POWER SUPPLY CARD in slot PS 24, ADJUST to obtain 90.0 Vdc (88.0 to 92.0 Vdc) on DMM.	________

IF INOP light on IRM drawer remains ILLUMINATED, THEN

ADJUST Z32-R1 until INOP indicating light on IRM drawer EXTINGUISHES.  Otherwise, MARK N/A.	________

ADJUST Z32-R1 until INOP indicating light on IRM drawer is ILLUMINATED.	________

ADJUST R1 on POWER SUPPLY CARD in slot PS 24 until IRM INOP indicating light is EXTINGUISHED.	________

ADJUST R1 on POWER SUPPLY CARD in slot PS 24 until IRM INOP indicating light is ILLUMINATED.	________

IF IRM INOP trip is NOT 90.0 Vdc (88.0 to 92.0 Vdc), THEN

REPEAT Steps 6.10[12] through 6.10[15] until IRM INOP trip is within 88.0 to 92.0 Vdc.  Otherwise, MARK N/A.	________

RECORD As-left INOP trip voltage in Table 10.	________

Using R1 on POWER SUPPLY CARD PS 24, ADJUST to obtain 100.0 Vdc (99.0 to 101.0 Vdc) reading on DMM.	________

RECORD As-left high voltage reading in Table 9.	________

DISCONNECT HV-1, Special High Voltage Test box, from J7 in IRM drawer.	________

CONNECT high voltage cable to J7.	________

As-Left Trip Setpoints

IF all As-found trip setpoints in Table 1 are within tolerance AND NEITHER VOLTAGE PREREGULATOR Module VR27 (Table 3) NOR VOLTAGE REGULATOR Module VR29 (Table 4) was adjusted, THEN

PERFORM the following, otherwise, MARK steps N/A:

RECORD As-found values from Table 1 in As-left column of Table 1 for DOWNSCALE, UPSCALE HIGH, and UPSCALE HIGH HIGH trip setpoints.	________

MARK Steps 6.11[2] through 6.11[36] N/A.	________

DISCONNECT preamp input cable from J1 in IRM drawer.	________

MINIMIZE voltage output using amplitude controls on test oscillator.	________

ADJUST oscillator output frequency to 100 KHz.	________

CONNECT test oscillator to J1 in IRM drawer.	________

CONNECT J4 adapter to J4 on rear of IRM drawer.	________

CONNECT DMM to J4 adapter test jacks H(+) and K(-).	________

IF As-found DOWNSCALE trip setpoint in Table 1 is within tolerance AND NEITHER VOLTAGE PREREGULATOR Module VR27 (Table 3) NOR VOLTAGE REGULATOR Module VR29 (Table 4) was adjusted, THEN

PERFORM the following, otherwise, MARK steps N/A:

RECORD As-found value from Table 1 in As-left column of Table 1 for DOWNSCALE trip setpoint.	________

MARK Steps 6.11[9] through 6.11[15] N/A.	________

ADJUST test oscillator amplitude until DMM indicates 0.060 Vdc (0.048 to 0.072 Vdc).	________

IF IRM DOWNSCALE indicating light is ILLUMINATED, THEN

ADJUST Z32-R2 until indicating light is EXTINGUISHED.  Otherwise, MARK N/A.	________

ADJUST Z32-R2 until IRM DOWNSCALE indicating light is ILLUMINATED.	________

ADJUST test oscillator until front panel meter indicates 15 UNITS on black scale.	________

LOWER test oscillator output amplitude until IRM DOWNSCALE indicating light is ILLUMINATED.	________

IF DOWNSCALE trip point is NOT within 0.048 to 0.072 Vdc, THEN

REPEAT Steps 6.11[9] through 6.11[13] until DOWNSCALE trip point is within 0.048 to 0.072 Vdc.  Otherwise, MARK N/A.	________

RECORD As-left DOWNSCALE trip voltage in Table 1.	________

IF As-found UPSCALE HIGH trip setpoint in Table 1 is within tolerance AND NEITHER VOLTAGE PREREGULATOR Module VR27 (Table 3) NOR VOLTAGE REGULATOR Module VR29 (Table 4) was adjusted, THEN

PERFORM the following, otherwise, MARK steps N/A:

RECORD As-found value from Table 1 in As-left column of Table 1 for UPSCALE HIGH trip setpoint.	________

MARK Steps 6.11[17] through 6.11[22] N/A.	________

ADJUST test oscillator amplitude until DMM indicates 0.720 Vdc (0.700 to 0.740 Vdc).	________

NOTES

Steps 6.11[18.1] through 6.11[18.5] may be performed sequentially without signing each individual step until completion of the last step. Steps 6.11[18.2] through 6.11[18.4] are performed with the Reset switch held in the rotated position.

IF IRM drawer UPSCALE HIGH indicating light is ILLUMINATED, THEN 

PERFORM the following, otherwise, MARK steps N/A:

HOLD RESET switch in the RESET position.	________

ADJUST Z32-R3 until UPSCALE HIGH indicating light is EXTINGUISHED.	________

ADJUST Z32-R3 until UPSCALE HIGH indicating light is ILLUMINATED.	________

ADJUST test oscillator until front panel meter indicates 80 UNITS on black scale.	________

RELEASE RESET switch on IRM drawer.	________

CHECK UPSCALE HIGH indicating light is EXTINGUISHED.	________

RAISE test oscillator output amplitude until UPSCALE HIGH indicating light is ILLUMINATED.	________

IF UPSCALE HIGH trip point is NOT 0.720 Vdc (0.700 to 0.740 Vdc), THEN

REPEAT Steps 6.11[17] through 6.11[20] until UPSCALE HIGH trip point is within 0.700 to 0.740 Vdc.  Otherwise, MARK N/A.	________

RECORD As-left UPSCALE HIGH trip voltage in Table 1.	________

IF As-found UPSCALE HIGH HIGH trip setpoint in Table 1 is within tolerance AND NEITHER VOLTAGE PREREGULATOR Module VR27 (Table 3) NOR VOLTAGE REGULATOR Module VR29 (Table 4) was adjusted, THEN

PERFORM the following, otherwise, MARK steps N/A:

RECORD As-found value from Table 1 in As-left column of Table 1 for UPSCALE HIGH HIGH trip setpoint.	________

MARK Steps 6.11[24] through 6.11[32] N/A.	________

ADJUST test oscillator amplitude until DMM indicates 0.931 Vdc (0.911 to 0.951 Vdc).	________

NOTES

Steps 6.11[25.1] through 6.11[25.5] may be performed sequentially without signing each individual step until completion of the last step. Steps 6.11[25.2] through 6.11[25.4] are performed with the Reset switch held in the rotated position.

IF UPSCALE HIGH HIGH indicating light is ILLUMINATED, THEN

PERFORM the following, otherwise, MARK steps N/A:

HOLD RESET switch in RESET position.	________

ADJUST Z32-R4 until UPSCALE HIGH HIGH indicating light is EXTINGUISHED.	________

ADJUST Z32-R4 until UPSCALE HIGH HIGH indicating light is ILLUMINATED.	________

ADJUST test oscillator until front panel meter indicates 110 UNITS on black scale.	________

RELEASE RESET switch on IRM drawer.	________

CHECK UPSCALE HIGH HIGH indicating light is EXTINGUISHED.	________

RAISE test oscillator output amplitude until UPSCALE HIGH HIGH indicating light is ILLUMINATED.	________

IF UPSCALE HIGH HIGH trip setpoint is NOT 0.931 Vdc (0.911 to 0.951 Vdc), THEN

REPEAT Steps 6.11[24] through 6.11[27] until UPSCALE HIGH HIGH trip point is within 0.911 to 0.951 Vdc.  Otherwise, MARK N/A.	________

RECORD As-left UPSCALE HIGH HIGH trip voltage in Table 1.	________

ADJUST test oscillator until front panel meter indicates 110 UNITS on black scale.	________

Using RESET switch on IRM drawer, RESET local IRM alarms.	________

CHECK UPSCALE HIGH HIGH indicating light is EXTINGUISHED.	________

REMOVE DMM.	________

IF NOT performing Section 6.12, THEN

REMOVE J4 adapter.  Otherwise, MARK N/A.	________

REMOVE test oscillator from J1 at back of IRM.	________

CONNECT preamp input cable J1 at rear of IRM drawer.	________

IF NOT performing Section 6.12, THEN

CONNECT recorder cable to J4 at rear of IRM drawer.  Otherwise, MARK N/A.	________

IRM System Gain and Range Correlation

DISCONNECT high voltage cable from J7 at back of IRM Drawer.	________

PERFORM the following at Panel 2-LPNL-925-0027 (located at EL 565', R10-S Line):

DISCONNECT INPUT cable from J-1 on 2-AMP-092-0007/41A, IRM CH A PREAMP.	________

DISCONNECT OUTPUT cable from J-2 on IRM-A preamp.	________

DISCONNECT HV input cable from J-3 on IRM-A preamp.	________

DISCONNECT LOW VOLTAGE input cable from J-4 on IRM-A preamp.	________

REMOVE IRM-A preamp from Panel 2-LPNL-925-0027.	________

MOVE IRM-A preamp to Unit 2 Control Room.	________

DISCONNECT preamp input cable from J-1 on IRM drawer.	________

DISCONNECT low voltage cable from J-42 on IRM drawer.	________

IF AMPLIFIER & ATTENUATOR Module AR11 is 194X667 G1, THEN

PERFORM the following, otherwise, MARK steps N/A:

REMOVE AMPLIFIER & ATTENUATOR Module AR11 from IRM drawer.	________

IF AMPLIFIER & ATTENUATOR Module AR11 R19 or R1 is NOT accessible, THEN

REMOVE cover from AMPLIFIER & ATTENUATOR Module AR11.  Otherwise, MARK N/A.	________

INSTALL AMPLIFIER & ATTENUATOR Module AR11 on GE129B2048G2 plug-in adapter.	________

INSTALL AMPLIFIER & ATTENUATOR Module AR11 with GE129B2048G2 plug-in adapter in AMPLIFIER & ATTENUATOR Module AR11 location in IRM drawer.	________

CONNECT test equipment as shown on Attachment 4, Test Setup For IRM Channel Calibration.	________

REQUEST UO place 2-XS-92-7/42A, CHANNEL A IRM RANGE SWITCH, to Range 6 Position.	________

PLACE Test Attenuator switch S1 in Position 6.	________

ADJUST test oscillator for 8 KHz output.	________

ADJUST test oscillator amplitude to produce a midscale indication on IRM front panel meter.	________

ADJUST output frequency between 8 and 16 KHz, while maintaining constant output amplitude from test oscillator, until a minimum indication is observed on DMM.	________

ADJUST amplitude of test oscillator to 2.29 mV as read on RMS voltmeter.	________

ADJUST R19 or R1 on AMPLIFIER & ATTENUATOR Module AR11 until DMM connected to IRM drawer indicates same voltage calculated in Step 6.9[33].	________

RECORD As-left voltage from previous step in space below.

| ______________ Vdc. |  | ________ |
| --- | --- | --- |

DISCONNECT DMM at IRM drawer.	________

CONNECT J4 adapter to J4.	________

CONNECT DMM to J4 adapter H(+) and K(-).	________

ADJUST R10 on FEEDBACK UNIT Z14 for 1.000 Vdc (0.990 to 1.010 Vdc) indication on DMM.	________

RECORD As-left voltage in Table 11.	________

| Table 11 |  |  |  |
| --- | --- | --- | --- |
| Desired Vdc | Min Vdc | As-left Vdc | Max Vdc |
| 1.000 | 0.990 |  | 1.010 |

PLACE IRM drawer Mode switch to 125 position.	________

IF Vdc is NOT in range of 0.990 to 1.010 Vdc, THEN

ADJUST R9 on Diode Logic and Calibration Unit Z10 for 1.000 Vdc (0.990 to 1.010 Vdc) indication on DMM.  Otherwise, MARK N/A.	________

RECORD As-left voltage in Table 12.	________

| Table 12 |  |  |  |
| --- | --- | --- | --- |
| Desired Vdc | Min Vdc | As-left Vdc | Max Vdc |
| 1.000 | 0.990 |  | 1.010 |

PLACE IRM drawer Mode switch to 40 position.	________

RECORD As-left voltage in Table 13.	________

| Table 13 |  |  |  |
| --- | --- | --- | --- |
| Desired Vdc | Min Vdc | As-left Vdc | Max Vdc |
| 0.316 | 0.306 |  | 0.326 |

IF AMPLIFIER & ATTENUATOR Module AR11 is 194X667 G1, THEN

PERFORM the following, otherwise, MARK steps N/A.

REMOVE AMPLIFIER & ATTENUATOR Module AR11 and plug-in adapter from IRM drawer.	________

IF AMPLIFIER & ATTENUATOR Module AR11 cover was removed, THEN

REPLACE cover.  Otherwise, MARK N/A.	________

REINSTALL AMPLIFIER & ATTENUATOR Module AR11, without GE129B2048G2 plug-in adapter, in AMPLIFIER & ATTENUATOR Module AR11 location in IRM drawer.	________

DISCONNECT test oscillator from IRM TEST FIXTURE.	________

PLACE IRM drawer Mode switch to OPERATE position.	________

NOTE

Steps 6.12[29] through 6.12[32] may be performed sequentially without signing each individual step until completion of the last step.

REQUEST UO place 2-XS-92-7/42A, CHANNEL A IRM RANGE SWITCH, to range Position 1.	________

PLACE IRM TEST FIXTURE switch to range Position 1.	________

RECORD DMM reading for Range 1 in Noise Only column of Attachment 5, Range Switch Signal Acceptance, Table 14.	________

REPEAT Steps 6.12[29] through 6.12[31] for ranges 2 through 6.	________

ENSURE 2-XS-92-7/42A, CHANNEL A IRM RANGE SWITCH is in Position 6.	________

ENSURE Test Attenuator switches are in Position 6.	________

CONNECT test oscillator to J1 on Test Attenuator portion of IRM TEST FIXTURE.	________

ADJUST test oscillator output frequency to 8 KHz.	________

ADJUST test oscillator amplitude to produce a midscale indication on IRM front panel meter.	________

ADJUST output frequency between 8 and 16 KHz, while maintaining constant output amplitude from test oscillator, until a maximum indication is observed on DMM.	________

ADJUST Amplitude control of test oscillator to obtain a 1.000 Vdc (0.995 to 1.005 Vdc) reading on DMM.	________

RECORD RMS voltage signal in space below.

| ______________ mVac. |  | ________ |
| --- | --- | --- |

NOTE

Steps 6.12[41] through 6.12[45] may be performed sequentially without signing each individual step until completion of the last step.

MAINTAIN test oscillator output level to value recorded in Step 6.12[40] during the performance of the following steps.	________

REQUEST UO place 2-XS-92-7/42A, CHANNEL A IRM RANGE SWITCH, to range Position 1.	________

PLACE  IRM TEST FIXTURE switch to range Position 1.	________

RECORD DMM reading for Range 1 in Noise (+) Signal column of Attachment 5, Range Switch Signal Acceptance, Table 14.	________

REPEAT Steps 6.12[42] through 6.12[44] for ranges 2 through 6.	________

DISCONNECT test oscillator from test attenuator.	________

SUBTRACT Noise Only DMM readings from Noise (+) Signal readings for Ranges 1 through 6 on Attachment 5, Range Switch Signal Acceptance, Table 14.	________
	________
	IV

RECORD Ranges 1 through 6 results in Signal Only columns on Attachment 5, Range Switch Signal Acceptance, Table 14.	________

RECORD highest Signal Only voltage for Ranges 1 through 6 on Attachment 5, Range Switch Signal Acceptance, Table 14.	________

RECORD lowest Signal Only voltage for Ranges 1 through 6 on Attachment 5, Range Switch Signal Acceptance, Table 14.	________

SUBTRACT lowest Signal Only voltage from highest Signal Only voltage for Ranges 1 through 6.	________
	________
	IV

RECORD results on Attachment 5, Range Switch Signal Acceptance, Table 14.	________

NOTE

A problem exists with the IRM or the test equipment setup if value calculated in Step 6.12[52] is greater than 0.060 Vdc.

IF value calculated in Step 6.12[52] is greater than 0.060 Vdc, THEN

PERFORM the following, otherwise, MARK steps N/A:

CHECK test equipment setup.	________

REPEAT Steps 6.12[29] through 6.12[52]	________

IF repeating Steps 6.12[29] through 6.12[52] does NOT result in a value equal to or less than 0.060 Vdc, THEN

NOTIFY Instrument Foreman or Cognizant Engineer for direction prior to continuing this procedure.  Otherwise, MARK N/A.	________

DISCONNECT capacitor from test attenuator.	________

NOTE

Steps 6.12[56] through 6.12[59] may be performed sequentially without signing each individual step until completion of the last step.

REQUEST UO place 2-XS-92-7/42A, CHANNEL A IRM RANGE SWITCH, to range Position 7.	________

PLACE IRM TEST FIXTURE switch to range Position 7.	________

RECORD DMM reading for Range 7 in Noise Only column of Attachment 5, Range Switch Signal Acceptance, Table 14.	________

REPEAT Steps 6.12[56] through 6.12[58] for ranges 8 through 10.	________

CONNECT test oscillator to J1 on IRM TEST FIXTURE.	________

REQUEST UO at 2-XS-92-7/42A, CHANNEL A IRM RANGE SWITCH, and IM at IRM TEST FIXTURE place respective switches to Range 7.	________

ADJUST test oscillator frequency to 350 KHz.	________

ADJUST test oscillator amplitude output level to produce a midscale indication on IRM front panel meter.	________

ADJUST output frequency between 350 and 450 KHz, while maintaining constant output amplitude from test oscillator, until a maximum indication is observed on DMM.	________

ADJUST Amplitude control of test oscillator to obtain a 1.000 Vdc (0.995 to 1.005 Vdc) reading on DMM.	________

RECORD RMS voltage signal in space below.

|  | mVAC |  | ________ |
| --- | --- | --- | --- |

RECORD DMM reading for Range 7 in Noise (+) Signal column of Attachment 5, Range Switch Signal Acceptance, Table 14.	________

NOTE

Steps 6.12[68] through 6.12[72] may be performed sequentially without signing each individual step until completion of the last step.

MAINTAIN test oscillator output level to value recorded in Step 6.12[66] during the performance of the following steps.	________

REQUEST UO place 2-XS-92-7/42A, CHANNEL A IRM RANGE SWITCH, to range Position 8.	________

PLACE IRM TEST FIXTURE switch to range Position 8.	________

RECORD DMM reading for Range 8 in Noise (+) Signal column of Attachment 5, Range Switch Signal Acceptance, Table 14.	________

REPEAT Steps 6.12[69] through 6.12[71] for ranges 9 and 10.	________

SUBTRACT Noise Only DMM readings for Ranges 7 through 10 from Noise (+) Signal readings on Attachment 5, Range Switch Signal Acceptance, Table 14.	________
	________
	IV

RECORD results in Signal Only for Ranges 7 through10 columns on Attachment 5, Range Switch Signal Acceptance, Table 14.	________

RECORD highest Signal Only voltage for Ranges 7 through 10 on Attachment 5, Range Switch Signal Acceptance, Table 14.	________

RECORD lowest Signal Only voltage for Ranges 7 through 10 on Attachment 5, Range Switch Signal Acceptance, Table 14.	________

SUBTRACT lowest Signal Only voltage from highest Signal Only voltage for Ranges 7 through 10.	________
	________
	IV

RECORD results on Attachment 5, Range Switch Signal Acceptance, Table 14.	________

NOTE

A problem exists with the IRM or the test equipment setup if value calculated in Step 6.12[77] is greater than 0.060 Vdc.

IF value calculated in Step 6.12[78] is greater than 0.060 Vdc, THEN

PERFORM the following, otherwise, MARK steps N/A:

CHECK test equipment setup.	________

DISCONNECT test oscillator from test attenuator.	________

REPEAT Steps 6.12[56] through 6.12[78].	________

IF repeating Steps 6.12[56] through 6.12[78] does NOT result in a value equal to or less than 0.060 Vdc, THEN

NOTIFY Instrument Foreman or Cognizant Engineer for direction prior to continuing this procedure.  Otherwise, MARK N/A.	________

DISCONNECT all test equipment from IRM preamp.	________

PERFORM the following at Panel 2-LPNL-925-0027:

INSTALL IRM-A preamplifier in 2-LPNL-925-0027.	________

TORQUE, with Peer Check, four IRM-A preamplifier retaining nuts to 20 in-lbs each.	________

CONNECT LOW VOLTAGE cable to J4 on IRM preamp.	________

CONNECT OUTPUT cable to J2 on IRM preamp.	________

CONNECT INPUT cable to J1 on IRM preamp.	________

CONNECT HV cable to J3 on IRM preamp.	________

CONNECT high voltage cable to J7 in IRM drawer.	________

DISCONNECT test cable from J42 in IRM drawer.	________

CONNECT low voltage cable to J42.	________

ADJUST amplitude controls on test oscillator for minimum voltage input.	________

ADJUST oscillator output frequency to 100 KHz.	________

Using BNC-T connector, CONNECT RMS Voltmeter to test oscillator 600 output cable.	________

CONNECT test oscillator to J1 in IRM drawer.	________

REQUEST UO ensure 2-XS-92-7/42A, CHANNEL A IRM RANGE SWITCH, in Position 2.	________

RECORD RMS Voltmeter value below that was recorded in Step 6.3[33].

| ______________ mVac. |  | ________ |
| --- | --- | --- |

ADJUST oscillator amplitude until RMS Voltmeter indicates value recorded in Step 6.12[91].	________

IF DMM value is within allowable range of 0.990 Vdc to 1.010 Vdc, THEN

MARK Steps 6.12[94] through 6.12[96.3] N/A.  Otherwise, MARK N/A.	________

IF AMPLIFIER & ATTENUATOR Module AR11 is 194X667 G1, THEN

PERFORM the following, otherwise, MARK steps N/A:

REMOVE AMPLIFIER & ATTENUATOR Module AR11 from IRM drawer.	________

IF AMPLIFIER & ATTENUATOR Module AR11 R19 or R1 is NOT accessible, THEN

REMOVE cover from AMPLIFIER & ATTENUATOR Module AR11.  Otherwise, MARK N/A.	________

INSTALL AMPLIFIER & ATTENUATOR Module AR11 on GE129B2048G2 plug-in adapter.	________

INSTALL AMPLIFIER & ATTENUATOR Module AR11, with plug-in adapter, in AMPLIFIER & ATTENUATOR Module AR11 location in IRM drawer.	________

ADJUST gain pot R19 on Amplifier and Attenuator board until DMM indication is 1.000 Vdc (0.990 Vdc to 1.010 Vdc) or gain pot is adjusted for maximum gain.	________

IF AMPLIFIER & ATTENUATOR Module AR11 is 368X189AA G001 or G002, THEN

ADJUST gain pot R1 on Amplifier and Attenuator board until DMM indication is 1.000 Vdc (0.990 Vdc to 1.010 Vdc) or gain pot is adjusted for maximum gain.  Otherwise, MARK N/A.	________

IF AMPLIFIER & ATTENUATOR Module AR11 is 194X667 G1, THEN

PERFORM the following, otherwise, MARK steps N/A:

REMOVE AMPLIFIER & ATTENUATOR Module AR11 and plug-in adapter from IRM drawer.	________

IF AMPLIFIER & ATTENUATOR Module AR11 cover was removed THEN

REPLACE cover.  Otherwise, MARK N/A.	________

INSTALL AMPLIFIER & ATTENUATOR Module AR11, without plug-in adapter, in AMPLIFIER & ATTENUATOR Module AR11 location in IRM drawer.	________

DISCONNECT test oscillator from J1 in IRM drawer.	________

CONNECT test oscillator to J1 of test attenuator.	________

PLACE IRM drawer Mode switch to 125 position.	________

IF DMM is NOT indicating 0.990 to 1.010 Vdc, THEN

ADJUST R9 on DIODE LOGIC & CALIBRATION Unit Z10 to obtain 1.000 Vdc (0.990 to 1.010 Vdc) on DMM.  Otherwise, MARK N/A.	________

RECORD As-left Vdc below.

| As-left Vdc _______________ |  | ________ |
| --- | --- | --- |

PLACE IRM drawer Mode switch to OPERATE.	________

CONNECT preamp input cable to J1 in IRM drawer.	________

DISCONNECT high voltage cable from J-7 in IRM drawer.	________

PERFORM the following at 2-LPNL-925-0027:

DISCONNECT HV cable from J-3 at IRM A preamp.	________

DISCONNECT INPUT cable from J-1 at IRM A preamp.	________

Utilizing BNC/HN adapter, CONNECT High Voltage input cable to preamp at J-1(Signal Input).	________

At IRM drawer, utilizing BNC/Barrel adapter, CONNECT test attenuator output (J-3) to high voltage cable coming to IRM drawer.	________

PERFORM the following:

REQUEST UO place 2-XS-92-7/42A, CHANNEL A IRM RANGE SWITCH, in Position 1.	________

PLACE IRM TEST FIXTURE range switch (S1) in Position 1.	________

NOTES

Noise levels on lower ranges may cause OFFSCALE indication on IRM drawer. Increased IRM indication is expected when UO selects Range 7.

ADJUST oscillator output amplitude for 50% indication on UNITS scale of IRM drawer front panel meter.	________

REQUEST UO place 2-XS-92-7/42A, CHANNEL A IRM RANGE SWITCH, in next higher range position.	________

NOTE

A decreasing IRM indication upon selection of next higher range demonstrates IRM is attenuating.

CHECK decreased IRM indication.	________

SELECT next higher range at IRM TEST FIXTURE to match range selected by UO in Step 6.12[107.4].	________

REPEAT Steps 6.12[107.3] through 6.12[107.6] for ranges 2 through 10.	________

DISCONNECT BNC/Barrel adapter from high voltage cable.	________

PERFORM the following at 2-LPNL-925-0027:

DISCONNECT BNC/HN adapter and cable from J-1 at preamp.	________

CONNECT HV cable to J-3 at preamp.	________

CONNECT INPUT cable to J-1 on IRM preamp.	________

CONNECT high voltage cable to J-7 in IRM drawer.	________

DISCONNECT test equipment from J4 in IRM drawer.	________

CONNECT recorder cable to J4.	________

PLACE IRM drawer Mode switch to 40 position.	________

CHECK IRM CH A, CH 3 of Recorder 2-XR-92-7/46A, IRM-APRM LEVEL, on Panel 2-9-5 indicates between 38 and 42.	________

IF recorder indication is NOT between 38 and 42, THEN

INITIATE CR to calibrate or repair recorder.  Otherwise, MARK N/A.	________

CHECK computer point IRM A indicates between 38 and 42.	________

IF computer is OPERABLE AND computer point IRM A does NOT indicate between 38 and 42, THEN

INITIATE CR.  Otherwise, MARK N/A.	________

PLACE IRM drawer Mode switch to 125 position.	________

CHECK computer point IRM A indicates between 123 and 127.	________

IF computer is OPERABLE AND computer point IRM A does NOT indicate between 123 and 127, THEN

INITIATE CR.  Otherwise, MARK N/A.	________

CLOSE IRM drawer.	________

PLACE IRM drawer Mode switch to OPERATE.	________

RESET IRM alarms using RESET switch on IRM drawer.	________

REQUEST UO place 2-XS-92-7/42A, CHANNEL A IRM RANGE SWITCH, to a position appropriate for current plant conditions.	________

Functional Test of IRM Channel A with Reactor Mode Switch in RUN

IF Reactor Mode Switch is in RUN, THEN

CONTINUE.  Otherwise, MARK Steps 6.13[2] through 6.13[23] N/A.	________

CHECK the following conditions exist for IRM Channel A:	________

IRM HIGH HIGH OR INOP indicating light is EXTINGUISHED on Panel 2-9-5.	________

IRM HIGH indicating light is EXTINGUISHED on Panel 2-9-5.	________

IRM BYPASSED indicating light is EXTINGUISHED on Panel 2-9-5.	________

IRM drawer Mode switch in OPERATE.	________

IRM drawer INOP indicating light is EXTINGUISHED.	________

IRM drawer UPSCALE HIGH indicating light is EXTINGUISHED.	________

IRM drawer UPSCALE HIGH HIGH indicating light is EXTINGUISHED.	________

PLACE IRM drawer Mode switch to ZERO 2 position.	________

CHECK the following on IRM drawer:

INOP light ILLUMINATED.	________

Front panel meter indicates 0 UNITS.	________

IF computer is OPERABLE, THEN

CHECK Computer point IRM A indicates 0.  Otherwise, MARK N/A.	________

PLACE IRM drawer Mode switch to 125 position.	________

CHECK the following:

IRM drawer UPSCALE HIGH indicating light is ILLUMINATED.	________

IRM drawer UPSCALE HIGH HIGH indicating light is ILLUMINATED.	________

IRM drawer front panel meter indicates 125 UNITS (123 to 125 UNITS).	________

CH 3 of Recorder 2-XR-92-7/46A, IRM-APRM LEVEL, indicates 125 (123 to 127) on Panel 2-9-5.	________

IF ICS computer is OPERABLE, THEN

CHECK ICS Computer point IRM A indicates 125 (123 to 127).  Otherwise, MARK N/A.	________

PLACE IRM drawer Mode switch to 40 position.	________

CHECK IRM drawer front panel meter indicates between 38 and 42 UNITS.	_____(AC)

CHECK IRM drawer DOWNSCALE indicating light is EXTINGUISHED on Panel 2-9-12.	________

IF ICS computer is OPERABLE, THEN

CHECK Computer point IRM A indicates 38 to 42.  Otherwise, MARK N/A.	________

PLACE IRM drawer Mode switch to ZERO 1 position.	________

CHECK the following on IRM drawer:

DOWNSCALE indicating light is ILLUMINATED.	________

Front panel meter indicates 0 UNITS.	________

RESET local IRM alarms using RESET switch on IRM drawer.	________

CHECK the following on IRM drawer:

UPSCALE HIGH indicating light is EXTINGUISHED.	________

UPSCALE HIGH HIGH indicating light is EXTINGUISHED.	________

PLACE IRM drawer Mode switch to OPERATE position.	________

RESET local IRM alarms using RESET switch on IRM drawer.	________

CHECK the following on IRM drawer:

INOP indicating light is EXTINGUISHED.	________

UPSCALE HIGH indicating light is EXTINGUISHED.	________

UPSCALE HIGH HIGH indicating light is EXTINGUISHED.	________

REQUEST UO or designee annotate the following at Recorder 2-XR-92-7/46A Channel 3 on Panel 2-9-5:

Channel 3

2-SR-3.3.1.1.9(IRM A)

Initials	________

REQUEST UO remove IRM A from BYPASS by removing 2-HS-92-7A/S4A, IRM BYPASS from CH-A Position.	________

CHECK BYPASS IRM CH A indicating light is EXTINGUISHED on Panel 2-9-12.	________

MARK Steps 6.14[1] through 6.14[68.3] N/A.	________

Functional Test of IRM Channel A with Reactor Mode Switch NOT in RUN

CHECK following conditions exist for CHANNEL A IRM:

IRM drawer Mode switch in OPERATE position.	________

IRM INOP indicating light is EXTINGUISHED on Panel 2-9-12.	________

IRM HIGH HIGH or INOP indicating light is EXTINGUISHED on Panel 2-9-5.	________

IRM HIGH indicating light is EXTINGUISHED on Panel 2-9-5.	________

IRM BYPASSED indicating light is ILLUMINATED on Panel 2-9-5.	________

IF CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7) is in ALARM, THEN

REQUEST UO clear CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7).  Otherwise, MARK N/A.	________

IF CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7) are NOT cleared, THEN

PERFORM the following, otherwise, MARK steps N/A:

CONNECT VOM #1 between terminal F-39 and F-41 in Panel 2-9-12 to monitor contact action.	________

CHECK VOM #1 connected in Step 6.14[3.1] indicates contacts are CLOSED.	________

CONNECT VOM #2 between terminal F-45 and F-46 in Panel 2-9-12 to monitor contact action.	________

CHECK VOM #2 connected in Step 6.14[3.3] indicates contacts are CLOSED.	________

NOTE

Steps 6.14[4] and 6.14[5] may be performed concurrently.

IF blue scram links are removed, THEN

PERFORM the following, otherwise, MARK steps N/A:

NOTIFY Unit SRO the following will be defeated for performance of this procedure:

Reactor manual scram Channel B3 function of SRM's A and C.

APRM 2-out-of-4 voter Channels 1 and 3.

IRM's A, C, E, and G.	________

CONNECT jumper between terminals CC-76 and CC-77, at Panel 2-9-15, Bay 2, in Auxiliary Instrument Room.	________
	________
	CV

RECORD date and time jumper was placed.

| Date: |  |  | Time: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |

IF red scram links are removed, THEN

PERFORM the following, otherwise, MARK steps N/A:

NOTIFY Unit SRO the following will be defeated for performance of this procedure:

Reactor manual scram Channel A3 function of SRM's A and C.

APRM 2-out-of-4 voter Channels 1 and 3.

IRM's A, C, E, and G.	________

CONNECT jumper between terminals CC-74 and CC-75 at Panel 2-9-15, Bay 2, in Auxiliary Instrument Room.	________
	________
	CV

RECORD date and time jumper was placed.

| Date: |  |  | Time: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |

NOTE

INOP/INHIBIT pushbutton in the next step remains PRESSED until Step 6.14[38].

PRESS and HOLD 2-HS-92-7/41A, IRM CHANNEL A INOP/INHIBIT pushbutton on IRM drawer until instructed to release it.	________

PLACE IRM drawer Mode switch to ZERO 2 position.	________

CHECK the following:

IRM drawer DOWNSCALE indicating light is ILLUMINATED.	________

IRM drawer front panel meter indicates 0 UNITS. (0 to 2 UNITS).	________

CH 3 of Recorder 2-XR-92-7/46A, IRM-APRM LEVEL, indicates 0 on Panel 2-9-5.	________

IF ICS computer is OPERABLE, THEN

CHECK Computer point IRM A indicates 0.  Otherwise, MARK N/A.	________

REQUEST UO place 2-XS-92-7/42A, CHANNEL A IRM RANGE SWITCH in Position 1.	________

IF IRM DOWNSCALE (2-XA-55-5A, window 19) is NOT in ALARM, THEN

NOTIFY UO IRM DOWNSCALE (2-XA-55-5A, window 19) is going to ALARM.  Otherwise, MARK N/A.	________

REQUEST UO remove IRM CHANNEL A from BYPASS by removing 2-HS-92-7A/S4A, IRM BYPASS from CH-A Position.	________

CHECK the following:

IRM BYPASSED indicating light is EXTINGUISHED on Panel 2-9-5.	________

IRM DNSCL indicating light is ILLUMINATED on Panel 2-9-5.	________

IRM DOWNSCALE (2-XA-55-5A, window 19) is in ALARM.	________

IRM drawer BYPASSED IRM indicating light is EXTINGUISHED on Panel 2-9-12.	________

IF ICS computer is OPERABLE AND no other IRM is bypassed, THEN

CHECK computer point DIG125 indicates NORMAL.  Otherwise, MARK N/A.	________

IF CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7) is NOT in ALARM, THEN

NOTIFY UO CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7) is going to ALARM.  Otherwise, MARK N/A.	________

REQUEST UO place 2-XS-92-7/42A, CHANNEL A IRM RANGE SWITCH in Position 2.	________

CHECK CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7) is in ALARM or VOM #1 connected in Step 6.14[3.1], indicates contacts OPEN.	_____(AC)

IF ICS computer is OPERABLE AND 2-HS-99-5A/S1 is NOT in SHUTDOWN, THEN

CHECK computer point DIG127 indicated TRIP.  Otherwise, MARK N/A.	________

REQUEST UO place IRM A in BYPASS by placing 2-HS-92-7A/S4A, IRM BYPASS in CH-A Position.	________

PLACE IRM drawer Mode switch to ZERO 1 position.	________

CHECK IRM drawer front panel meter indicates 0 UNITS.	________

IF any local IRM alarms are in ALARM, THEN

Using RESET switch on IRM drawer, RESET local IRM alarms.  Otherwise, MARK N/A.	________

REQUEST UO return 2-XS-92-7/42A, CHANNEL A IRM RANGE SWITCH to Position 1.	________

REQUEST UO remove IRM A from BYPASS by removing 2-HS-92-7A/S4A, IRM BYPASS from CH-A Position.	________

CHECK CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7) is CLEAR or if connected in Step 6.14[3.1], VOM #1 indicates contacts CLOSED.	________

IF CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7) is NOT in ALARM, THEN

NOTIFY UO CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7) is going to ALARM.  Otherwise, MARK N/A.	________

IF CRD platform is NOT in normal position OR IRM Cables are NOT routed in normal configuration, THEN

MONITOR IRM detector when being withdrawn.  Otherwise, MARK N/A.	________

REQUEST UO withdraw IRM A Detector until IRM A detector IN indicating light is EXTINGUISHED.	________

CHECK CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7) is in ALARM, or VOM #1 connected in Step 6.14[3.1], indicates contacts OPEN.	_____(AC)

IF ICS computer is OPERABLE, THEN

CHECK computer point DIG126 indicates ABNORMAL.  Otherwise, MARK N/A.	________

IF CRD platform is NOT in normal position OR IRM cables are NOT routed in normal configuration, THEN

MONITOR IRM detector when being inserted.  Otherwise, MARK N/A.	________

REQUEST UO insert IRM A Detector to FULL IN position.	________

CHECK IRM A detector IN indicating light is ILLUMINATED.	________

IF ICS computer is OPERABLE AND no other IRM is withdrawn, THEN

CHECK computer point DIG126 indicates NORMAL.  Otherwise, MARK N/A.	________

REQUEST UO reset affected annunciators.	________

CHECK CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7) is CLEAR, or VOM #1 connected in Step 6.14[3.1], indicates contacts CLOSED.	________

NOTIFY UO the following steps are going to result in a rod block, neutron monitoring system half scram, and associated annunciators.	________

RELEASE INOP/INHIBIT pushbutton on IRM drawer.	________

CHECK the following:

IRM drawer INOP indicating light is ILLUMINATED.	________

CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7) is in ALARM, or VOM #1 connected in Step 6.14[3.1], indicates contacts OPEN.	_____(AC)

SCRAM SOLENOID GROUP A LOGIC RESET indicating lights (4) are EXTINGUISHED on Panel 2-9-5.	_____(AC)

2-IL-99-5A/AB, SYSTEM A BACKUP SCRAM VALVE left indicating light is EXTINGUISHED on Panel 2-9-5.	________

2-IL-99-5A/CD, SYSTEM B BACKUP SCRAM VALVE left indicating light is EXTINGUISHED on Panel 2-9-5.	________

CHANNEL A IRM HIGH HIGH or INOP indicating light is ILLUMINATED on Panel 2-9-5.	________

IRM CHAN A, C, E, G HI-HI/INOP (2-XA-55-5A, window 33) is in ALARM.	________

NEUTRON MONITORING SYS HALF SCRAM (2-XA-55-4A, window 16) is in ALARM.	________

REACTOR CHANNEL A AUTO SCRAM (2-XA-55-5B, window 1) is in ALARM.	________

IF ICS computer is OPERABLE, THEN

PERFORM the following, otherwise, MARK steps N/A:

CHECK Computer point DIG129 indicates INOP.	________

CHECK Computer point SOE035 indicates TRIP.	________

REQUEST UO place IRM A in BYPASS by placing 2-HS-92-7A/S4A, IRM BYPASS in CH-A Position.	________

REQUEST UO reset half scram and associated annunciators.	________

CHECK the following:

SCRAM SOLENOID GROUP A LOGIC RESET indicating lights (4) are ILLUMINATED on Panel 2-9-5.	________

2-IL-99-5A/AB, SYSTEM A BACKUP SCRAM VALVE indicating lights (2) are ILLUMINATED on Panel 2-9-5.	________

2-IL-99-5A/CD, SYSTEM B BACKUP SCRAM VALVE indicating lights (2) are ILLUMINATED on Panel 2-9-5.	________

IRM HIGH HIGH OR INOP indicating light is EXTINGUISHED on Panel 2-9-5.	________

REACTOR CHANNEL A AUTO SCRAM (2-XA-55-5B, window 1) is CLEAR.	________

NEUTRON MONITORING SYS HALF SCRAM (2-XA-55-4A, window 16) is CLEAR.	________

IRM CHAN A, C, E, G HI-HI/INOP (2-XA-55-5A, window 33) is CLEAR.	________

CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7) is CLEAR, or VOM #1 connected in Step 6.14[3.1], indicates contacts CLOSED.	________

IF ICS computer is OPERABLE, THEN

PERFORM the following, otherwise, MARK steps N/A:

CHECK Computer point DIG129 indicates NORMAL.	________

CHECK Computer point SOE035 indicates NOTTRIP.	________

NOTE

INOP/INHIBIT pushbutton in the next step remains PRESSED until Step 6.14[60].

PRESS and HOLD 2-HS-92-7/41A, IRM CHANNEL A INOP/INHIBIT pushbutton on IRM drawer until instructed to release it.	________

IF IRM DOWNSCALE (2-XA-55-5A, window 19) is NOT in ALARM, THEN

NOTIFY UO IRM DOWNSCALE (2-XA-55-5A, window 19) is going to ALARM.  Otherwise, MARK N/A.	________

REQUEST UO remove IRM A from BYPASS by removing 2-HS-92-7A/S4A, IRM BYPASS from CH-A Position.	________

NOTIFY UO the following steps are going to result in a rod block, neutron monitoring system half scram, and associated annunciations.	________

PLACE IRM drawer Mode switch in 125 position.	________

CHECK the following:

IRM drawer UPSCALE HIGH indicating light is ILLUMINATED.	________

IRM drawer UPSCALE HIGH HIGH indicating light is ILLUMINATED.	________

IRM drawer front panel meter indicates 125 UNITS (123 to 125 UNITS).	________

IRM HIGH (2-XA-55-5A, window 26) is in ALARM.	________

IRM CHAN A, C, E, G HI-HI/INOP (2-XA-55-5A, window 33) is in ALARM.	________

CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7) is in ALARM, or VOM #2 connected in Step 6.14[3.3], indicates contacts OPEN.	_____(AC)

NEUTRON MONITORING SYS HALF SCRAM (2-XA-55-4A, window 16) is in ALARM.	________

REACTOR CHANNEL A AUTO SCRAM (2-XA-55-5B, window 1) is in ALARM.	________

SCRAM SOLENOID GROUP A LOGIC RESET indicating lights (4) are EXTINGUISHED on Panel 2-9-5.	_____(AC)

2-IL-99-5A/AB, SYSTEM A BACKUP SCRAM VALVE left indicating light is EXTINGUISHED on Panel 2-9-5.	________

2-IL-99-5A/CD, SYSTEM B BACKUP SCRAM VALVE left indicating light is EXTINGUISHED on Panel 2-9-5.	________

IRM CH A - CH 3 of Recorder 2-XR-92-7/46A indicates between 123 and 127 on Panel 2-9-5.	________

IRM HIGH indicating light is ILLUMINATED on Panel 2-9-5.	________

IRM HIGH HIGH OR INOP indicating light is ILLUMINATED on Panel 2-9-5.	________

IF ICS computer is OPERABLE, THEN

PERFORM the following, otherwise, MARK steps N/A:

CHECK Computer point DIG128 indicates HIGH.	________

CHECK Computer point SOE052 indicates TRIP.	________

REQUEST UO place IRM A in BYPASS by placing 2-HS-92-7A/S4A, IRM BYPASS in CH-A.	________

REQUEST UO reset half scram and associated annunciators.	________

CHECK the following:

SCRAM SOLENOID GROUP A LOGIC RESET indicating lights (4) are ILLUMINATED on Panel 2-9-5.	________

2-IL-99-5A/AB, SYSTEM A BACKUP SCRAM VALVE indicating lights (2) are ILLUMINATED on Panel 2-9-5.	________

2-IL-99-5A/CD, SYSTEM B BACKUP SCRAM VALVE indicating lights (2) are ILLUMINATED on Panel 2-9-5.	________

CHANNEL A IRM HIGH indicating light is EXTINGUISHED on Panel 2-9-5.	________

CHANNEL A IRM HIGH HIGH OR INOP indicating light is EXTINGUISHED on Panel 2-9-5.	________

CONTROL ROD WITHDRAWAL BLOCK (2-XA-55-5A, window 7) is CLEAR, or VOM #2 connected in Step 6.14[3.3], indicates contacts CLOSED.	________

IRM CHAN A, C, E, G HI-HI/INOP (2-XA-55-5A, window 33) is CLEAR.	________

IF ICS computer is OPERABLE, THEN

PERFORM the following, otherwise, MARK steps N/A:

CHECK Computer point DIG128 indicates NORMAL.	________

CHECK Computer point SOE052 indicates NOTTRIP.	________

PLACE IRM drawer Mode switch to 40 position.	________

CHECK IRM drawer front panel meter indicates between 38 and 42 UNITS.	_____(AC)

REQUEST UO place 2-XS-92-7/42A, CHANNEL A IRM RANGE SWITCH, in position required for current plant condition.	________

PLACE IRM drawer Mode switch to OPERATE.	________

RELEASE 2-HS-92-7/41A, IRM CHANNEL A INOP/INHIBIT pushbutton.	________

RESET local IRM alarms using RESET switch on IRM drawer.	________

CHECK the following IRM drawer indicating lights are EXTINGUISHED:

UPSCALE HIGH	________

UPSCALE HIGH HIGH	________

INOP	________

IF VOMs were connected in Steps 6.14[3.1] and 6.14[3.3], THEN

PERFORM the following, otherwise, MARK steps N/A:

REMOVE VOM #1 connected to terminals F-39 and F-41.	________

REMOVE VOM #2 connected to terminals F-45 and F-46.	________

REQUEST UO remove IRM A from BYPASS by removing 2-HS-92-7A/S4A, IRM BYPASS from CH-A Position.	________

CHECK IRM drawer BYPASS IRM Ch. A indicating light is EXTINGUISHED.	________

REQUEST UO or designee annotate the following at Recorder 2-XR-92-7/46A Channel 3 on Panel 2-9-5:

Channel 3

2-SR-3.3.1.1.9(IRM A)

Initials	________

NOTE

Steps 6.14[67] and 6.14[68] may be performed concurrently.

IF a jumper was installed in Step 6.14[4.2], THEN

PERFORM the following, otherwise, MARK steps N/A:

NOTIFY Unit SRO the following will be activated with removal of jumper:

Reactor manual scram Channel B3 function of SRM's A and C

APRM 2-out-of-4 voter Channels 1 and 3

IRM's A, C, E, and G	________

REMOVE jumper between terminals CC-76 and CC-77 at Panel 2-9-15, Bay 2, in Auxiliary Instrument Room.	________
	________
	IV

RECORD date and time jumper was removed.

| Date |  | Time |  |  |  |
| --- | --- | --- | --- | --- | --- |

IF a jumper was installed in Step 6.14[5.2], THEN

PERFORM the following, otherwise, MARK steps N/A:	________

NOTIFY Unit SRO the following will be activated with removal of jumper:

Reactor manual scram Channel A3 function of SRM's A and C.

APRM 2-out-of-4 voter Channels 1 and 3.

IRM's A, C, E, and G.	________

REMOVE jumper between terminals CC-74 and CC-75 at Panel 2-9-15, Bay 2, in Auxiliary Instrument Room.	________
	________
	IV

RECORD date and time jumper was removed.

| Date |  | Time |  |  |  |
| --- | --- | --- | --- | --- | --- |

POST PERFORMANCE ACTIVITY

Test Completion

RECORD date and time channel returned to service.

| Date |  | Time |  |  |  |
| --- | --- | --- | --- | --- | --- |

NOTIFY UO any INOPERABLE or bypassed IRM removed from BYPASS for performance of this procedure can be returned to mode required for current plant conditions.	________

RECORD M&TE Used (Y or N) in table in Step 4.2.2[2].	________

IF any AC was NOT satisfied, THEN

ENSURE CR is initiated.  Otherwise, MARK N/A.

| CR# | _________________________ |  | ________ |
| --- | --- | --- | --- |

NOTIFY UO procedure is complete.	________

NOTIFY Unit SRO procedure is complete.	________

RECORDS

All completed portions of this procedure and STS are to be maintained per NPG-SPP-31.2, Records Management.

Attachment 1

(Page 1 of 1)

Control Room Components Affected By Procedure Performance

| UNID | DESCRIPTION | LOCATION |
| --- | --- | --- |
| 2-XA-55-4A window 16 | NEUTRON MONITORING SYS HALF SCRAM | Panel 2-9-4 |
| 2-XA-55-5B window 1 | REACTOR CHANNEL A AUTO SCRAM | Panel 2-9-5 |
| 2-XA-55-5A window 19 | IRM DOWNSCALE | Panel 2-9-5 |
| 2-XA-55-5A window 26 | IRM HIGH | Panel 2-9-5 |
| 2-XA-55-5A window 33 | IRM CHAN A, C, E, G HI-HI/INOP | Panel 2-9-5 |
| 2-XA-55-5A window 7 | CONTROL ROD WITHDRAWAL BLOCK | Panel 2-9-5 |
|  | Indicating Lights (4 Red lights) - SCRAM SOLENOID GROUP A LOGIC RESET | Panel 2-9-5 |
|  | Indicating Light CHANNEL A IRM DNSCL | Panel 2-9-5 |
|  | Indicating Light CHANNEL A IRM HIGH | Panel 2-9-5 |
|  | Indicating Light CHANNEL A IRM HIGH HIGH or INOP | Panel 2-9-5 |
|  | Indicating Light CHANNEL A IRM BYPASSED | Panel 2-9-5 |
| 2-XR-092-7/46A | Recorder IRM-APRM LEVEL, CHANNEL A IRM -CH 3 | Panel 2-9-5 |
|  | ICS Computer Points |  |
| 2-IL-99-5A/AB | SYSTEM A BACKUP SCRAM VALVE Left Indicating Light | Panel 2-9-5 |
| 2-IL-99-5A/CD | SYSTEM B BACKUP SCRAM VALVE Left Indicating Light | Panel 2-9-5 |

Attachment 2

(Page 1 of 1)

TM200 To 2-RLY-92-741ATDR Test Setup

Attachment 3

(Page 1 of 1)

MSA Circuit Card Layout

Attachment 4

(Page 1 of 1)

Test Setup For IRM Channel Calibration

Attachment 5

(Page 1 of 1)

Range Switch Signal Acceptance

| Table 14 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Range switch Position | Noise (+) Signal (Vdc) | - | Noise Only (Vdc) | = | Signal Only | Acceptable Limit |
| 1 |  |  |  |  |  | Compare Ranges 1 through 6: |
| 2 |  |  |  |  |  | _______Vdc (Highest) |
| 3 |  |  |  |  |  | - ________Vdc (Lowest) |
| 4 |  |  |  |  |  | = ______Vdc ( 0.060 Vdc) |
| 5 |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |
| 7 |  |  |  |  |  | Compare Ranges 7 through 10: |
| 8 |  |  |  |  |  | _______Vdc (Highest) |
| 9 |  |  |  |  |  | - ________Vdc (Lowest) |
| 10 |  |  |  |  |  | = ______Vdc ( 0.060 Vdc) |